LOG BOOK FOR LEGIONELLA MANAGEMENT AND CONTROL

| MANAGEMENT INFORMATION |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Property: |  |  |  |  |  |
| Statutory duty holder: |  |  | Senior Manager oversees legionella management for the property |  |  |
| Name: |  |  | Email: |  | Phone: |
| Responsible person: |  |  | Fulfils the everyday requirements to manage and control legionella for the property – reports to the Senior Manager |  |  |
| Name: |  |  | Email: |  | Phone: |
| Operational person: |  |  | Supports the responsible person with every day requirements |  |  |
| Name: |  |  | Email: |  | Phone: |
| Operational person: |  |  | Supports the responsible person with every day requirements |  |  |
| Name: |  |  | Email: |  | Phone: |
| This log book provides a written scheme for controlling the legionella risk by implementing, managing and monitoring precautions and keeping records. This is in line with: HSE code of practise L8, Control of Legionella bacteria in water systems 2013; Health and Safety at Work etc Act 1974 sections 2, 3, 4; Control of Substances Hazardous to Health regulations 2002. |  |  |  |  |  |
| Monitoring: property risk assessment (which includes legionella risk assessment) reviewed annually by property manager; external property audit completed annually which includes viewing of HSV: 119 log book for legionella management and control |  |  |  |  |  |
| All records to be kept for 7 years in line with the Control of Substances Hazardous to Health regulations 2002 |  |  |  |  |  |

| ASSETS/ EQUIPMENT |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Cold water system |  | Hot water system |  |  |  |
| Ground floor | Source | Sentinel point | Source | Sentinel point | Condition | Insulated |

| RISK ASSESSMENT |  |  |  |
| --- | --- | --- | --- |
| LEGIONNAIRE RISK ASSESSMENT |  |  |  |
| Date: | Risk assessment completed by: | Actions complete | By who |
| Outstanding actions: |  |  |  |

| LEGIONNIARE RISK ASSESSMENT REVIEW – 2021 |  |  |  |  |
| --- | --- | --- | --- | --- |
| Date: | Risk assessment reviewed by: |  | Actions complete | By who |
|  | - Risk assessment reviewed, outstanding actions highlighted, management system developed to ensure legionella management and control in the property |  |  |  |
|  | - All actions completed |  |  |  |
|  | - Log book developed in line with L8 the control of legionella bacteria in water systems |  |  |  |
|  | - Hazardous substance risk assessment for property updated to include legionella |  |  |  |
|  | - Where needed training for Managers on legionella |  |  |  |
|  | Review of legionella management and control will be part of the annual review of the property risk assessment |  |  |  |
| List specific circumstances that may affect the scheme for controlling legionella? |  | What action has been agreed to reduce likelihood of legionella spreading to the property |  |  |
| e.g. Water supply fed from a tank in a neighbouring property |  | It has been agreed with the landlord that they must inform the property manager if it is to be empty. |  |  |

| LEGIONNIARE RISK ASSESSMENT REVIEW |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Record below when the annual review of the legionella section of the property risk assessment has been completed |  |  |  |  |  |
| Date: | Reviewed by: | Outstanding actions: |  | Actions complete | By who: |
| TRAINING RECORD |  |  |  |  |  |
| Legionella training for Managers, Volunteers as appropriate – copy of training package is in Appendix IV |  |  |  |  |  |
| Date: | Trainer |  | Attendee |  |  |

| WEEKLY MONITORING TASKS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EXAMPLES MIGHT INCLUDE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| How often | Checking for? |  | Checking what? |  |  |  |  |  |  |  |  | How to complete the check |  |  |  |  |  |  |  |  | Required outcome |  |  |  |  |
| Weekly | Cold water temperature, water not lying unused |  | Infrequent used outlet/ bib taps/ dead legs to be drained |  |  |  |  |  |  |  |  | Flush tap for 3 minutes then take temperature |  |  |  |  |  |  |  |  | Less than 20oC |  |  |  |  |
| If required temperature is not achieved check Appendix III for contingency measures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Week |  |  | Temperature oC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Location |  | 1 |  | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 |  | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 |  | 17 | 18 | 19 | 20 |

| MONTHLY MONITORING TASKS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EXAMPLES MIGHT INCLUDE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| How often | Checking for? |  | Checking what? |  |  |  |  | How to complete the check |  |  |  |  |  |  | Required outcome |  |  |  |
| Monthly | Hot water temperature |  | CB-1 combination boiler (sentinel outlet) |  |  |  |  | Flush water heater outlet for 1 minute and record temperature. |  |  |  |  |  | 50oC or more |  |  |  |  |
| Monthly | Cold water temperature |  | Tanked and mains cold water taps in sink or hand basin |  |  |  |  | Flush each cold tap for 2 minutes then take temperature |  |  |  |  |  |  | Less than 20oC |  |  |  |
| If required temperature is not achieved check Appendix III for contingency measures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | Temperature oC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Location |  | Year |  | Jan | Feb | Mar | Apr |  | May | Jun | Jul | Aug | Sep |  |  | Oct | Nov | Dec |

| SIX MONTHLY MONITORING TASKS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EXAMPLES MIGHT INCLUDE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| How often |  | Checking for? |  | Checking what? |  |  |  |  | How to complete the check |  |  |  |  |  |  |  |  |  | Required outcome |  |  |  |  |
| 6 monthly |  | Descale |  | Cold taps in kitchen sink and toilet hand basin |  |  |  |  | Inspect and if required dismantle, clean and de-scale tap heads |  |  |  |  |  |  |  |  |  | No scale |  |  |  |  |
| If required temperature is not achieved check Appendix III for contingency measures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Hot and cold taps descaled |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Check 1 |  |  |  |  |  |  |  |  | Check 2 |  |  |  |  |  |  |  |  |
| Location |  |  |  |  | Year | Jan | Feb | Mar |  | Apr |  | May | Jun |  | Jul | Aug |  | Sep |  | Oct |  | Nov | Dec |
| ANNUAL MONITORING TASKS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EXAMPLES MIGHT INCLUDE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| How often | Checking for? | Checking what? |  |  |  | How to complete the check |  |  |  |  |  |  |  |  |  |  |  | Required outcome |  |  |  |  |
| Annually | General inspection | CB-1 combination boiler |  |  |  | Visually inspect hot water heaters, arrange for remedial work to be carried out |  |  |  |  |  |  |  |  |  |  |  | No faults |  |  |  |  |
|  |  |  |  |  |  | CB-1 combination boiler |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Task |  |  |  |  |  | Year: |  |  |  | Year: |  |  | Year: |  |  | Year: |  |  |  | Year: |  |  |
| Capacity? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Unit ON/ OFF works satisfactorily? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| If OFF, is it isolated locally creating a dead leg? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Is the unit in regular use? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General condition |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Condition of associated pipework |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Flow temperature at the furthest outlet from this unit |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Signature: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| DEFECT LOG |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Fault acknowledged |  | Fault repaired |  |
| Asset/ location | Fault identified | Remedial work required | Date | Signature | Date | Signature |

| CONTRACTOR/ CONSULTANT/ VISITOR LOG |  |  |  |  |
| --- | --- | --- | --- | --- |
| Date | Name | Company/ organisation | Reason for visit | Signature |

APPENDIX I: RISK RATING

Example shown below:

| OVERALL RISK SCORE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Risk score allocation |  |  |  |  |  | Domestic cold water system |  |  |  |  |  | Domestic hot water system |  |  |  |  |  |
| Legionella Hazards | Year (20...) |  | 18 | 21 |  | 22 | 23 | 24 | 18 | 21 |  | 22 | 23 | 24 | 18 |  | 21 | 22 | 23 | 24 |
| Contamination |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 5. Legionella contamination |  |  | 1-5 |  |  |  |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  |
| 4. Bacterial contamination |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3. Untreated primary supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2. Fire systems sharing supply |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Treated water (e.g. town mains) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Amplification |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Poor temperature and/ or biocide levels |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Poor plant and/ or system conditions |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Non WRAS/ undesirable materials used |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  |
| Stagnation (little used outlets) |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |
| Poor system design |  |  | 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Management and PPM processes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Inadequate allocation of responsibilities |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  |
| Inadequate management documentation |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  |
| Inadequate PPM |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  |
| Inadequate record keeping |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  |
| Lack of suitable training |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  | 1 |  |  |  |  |  |
| HAZARD TOTAL |  |  | 0 – 15 |  |  |  |  |  | 8 |  |  |  |  |  | 7 |  |  |  |  |  |
| Likelihood of legionella |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Transmission |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - No domestic water present |  |  | 0 – 5 |  |  |  |  |  | 2 |  |  |  |  |  | 2 |  |  |  |  |  |
| - Bib taps |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Sinks/ hand basins/ WC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Emergency shower, swimming pool |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Irrigation, dental |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Adiabatic coolers, spray taps, showers, cooling towers, spa baths, ornamental fountains, dust suppression, vehicle wash etc. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Exposure – likelihood aerosols inhaled |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Unoccupied |  |  | 0 – 5 |  |  |  |  |  | 2 |  |  |  |  |  | 2 |  |  |  |  |  |
| - Aerosols contained/ removed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Aerosols possibly released |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Aerosols uncontained but little exposure |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Aerosols uncontained |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - High risk aerosols not contained |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Occupancy susceptibility |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Low |  |  | 1 – 5 |  |  |  |  |  | 2 |  |  |  |  |  | 2 |  |  |  |  |  |
| - Moderate |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - High |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Very high |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Extremely high |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| LIKELIHOOD TOTAL |  |  | 1 – 15 |  |  |  |  |  | 6 |  |  |  |  |  | 6 |  |  |  |  |  |
| OVERALL RISK RATING |  |  | 1 – 225 |  |  |  |  |  | 48 |  |  |  |  |  | 42 |  |  |  |  |  |
| RISK RATING RANGE |  | Low 1- 44 |  |  | Moderate 45 – 89 |  |  |  |  |  | High 90 -170 |  |  |  |  | Urgent 180 - 225 |  |  |  |  |

Risk score to be updated following annual audit

APPENDIX II: SCHEMATIC DRAWING

Example shown below:

APPENDIX III: CONTINGENCY MEASURES

| HOT AND COLD WATER TEMPERATURES |  |  |
| --- | --- | --- |
| If required temperature is not achieved check below for contingency measures |  |  |
| Task | Expected outcome | Possible contingency action if expected results not obtained |
| Checking cold water outlet temperature | Less than 20oC within 2 minutes of flushing | Flush outlet until temperature is reached, record time it takes to reach less than 20oC |
|  |  | If tank supply, check tank temperature including mains inlet |
|  |  | Check usage of outlet and add to infrequently used list for regular flushing |
|  |  | Check insulation on pipe work – repair or replace if in poor condition |
|  |  | Check if cold pipes are running above hot pipes adjacent heating system |
|  |  | Undertake legionella sampling if persistently above 20oC |
|  |  | Review risk assessment if problem persists |
| Checking Low volume point of use water heater <15 litres outlet temperature | Deliver 50oC within 1 minute | Increase thermostat/ control setting to achieve required temperature. |
|  |  | Specialist to inspect the equipment and carry out repairs or replace if required |

APPENDIX IV: LEGIONNAIRE TRAINING PACKAGE

APPENDIX V: SPECIALIST SERVICE AND VISIT REPORTS

APPENDIX VI: HSV: 124 - INCIDENT REPORT FOR CASE OR OUTBREAK OF LEGIONELLA